## Slide 1
“Building Energy Analysis” Course Notes – Fall 2021
Prepared by D. Mather
EA3: Aspects of Heat Transfer and Psychrometric
Analysis
1. Thermal Transmittance and Resistance of an Assembly
2. Thermal Resistances of Planar Layers
3. Steady 1D Heat Transmission through a Series of Planar Layers
4. Parallel Heat Transmission Paths
5. Heat Loss through Parallel Transmission and Ventilation
6. Nomenclature for Psychrometric Analysis
7. Psychrometric Chart
8. Basic Air-Conditioning Processes
Problems
Solutions

## Slide 2
Module Overview
This module provides a background in selected aspects of heat transfer and psychrometric analysis and discusses some aspects of HVAC systems. The content on heat transfer will be important in the upcoming module on Building Envelope. The content on psychrometric analysis is important for the analysis of air-based HVAC systems, including in simulation analysis.
For many students, some material will be a review of concepts previously covered in other courses.
Relevant Course Intended Learning Outcomes:
Apply basic energy calculations to a variety of components and systems impacting building energy use.
Apply simple analysis techniques in building energy auditing and simulation.
Recognize the interactive effects between different building components and systems as related to energy use.

## Slide 3
Aspects Of Heat Transfer

## Slide 4
Thermal Transmittance and Resistance of an Assembly
1.
Consider steady heat transfer between two environments (at temperatures and ) through an assembly of layers whose overall size normal to direction of heat transfer can be characterized by . We will restrict this discussion to situations where the heat transfer can be treated as one-dimensional (1D)—that is, temperatures vary only along dimension x (which point normal to the surface).
If the steady heat transfer rate is assessed using the thermal resistance method, the system might be represented by a thermal resistor separating two temperature nodes:
Here is the overall planar thermal resistance of the assembly separating and along the path crossing through area .
If expressed as an overall thermal transmittance of the assembly, , then:
has units or , with the temperature units (i.e. K or ) referring to the temperature difference between the two temperatures nodes. ( has the same value whether the units are indicated using K or .)
air
air

## Slide 5
is the inverse of :
Thus, the units of are , and the units of are .
Note that is an indicator of how readily an assembly allows heat flow (i.e. higher = higher heat flow), whereas indicates how readily an assembly resists heat flow (i.e. higher = lower heat flow).

## Slide 6
Thermal Resistances of Planar Layers
2.
1-D Steady Heat Conduction through a Planar Solid
Consider heat conduction occurring normal to the plane of surface area (i.e. along x-direction only; 1-D heat transfer).
3-D View
planar resistance of the layer
e.g. R-value of layer

## Slide 7
Example:
Consider a piece of extruded polystyrene insulation
Thickness = 25 mm
Rated Thermal Resistance: RSI-0.88
With this information we can calculate an estimate
of the thermal conductivity of the material.
Note: The “R-value” for a material is often listed in Inch-Pound units. For example, the photo below indicates “R-20” for a 4 inch thick insulation board.
The R-20 means the rated thermal resistance is 20 . The corresponding metric thermal resistance is called the RSI-value (where the “SI” indicates metric).
RSI = 20 / 5.678 = 3.52 . (5.678 = conversion factor)
RSI-value

## Slide 8
Approximate Thermal Conductivities of Selected Materials
(near “room temperature”, i.e. 300 K)
Material | Thermal conductivity, k
Aluminum (alloy 2014) |  192
Steel (alloy 1080) |  48
Stainless steel (alloy 31) |  16
Concrete |  0.9 to 2.9 (depends on density)
Soda Lime Glass (architectural glass) |  1.0
PVC (vinyl) |  0.18
Wood (spruce) |  0.09
Extruded Polystyrene Insulation (XPS) |  0.022 to 0.030
Material | 
Aluminum (alloy 2014) |  192
Steel (alloy 1080) |  48
Stainless steel (alloy 31) |  16
Concrete |  0.9 to 2.9 (depends on density)
Soda Lime Glass (architectural glass) |  1.0
PVC (vinyl) |  0.18
Wood (spruce) |  0.09
Extruded Polystyrene Insulation (XPS) |  0.022 to 0.030
W.D. Callister, “Materials Sciences and Engineering”, 3rd Edition, 1994
F.P. Incropera and D.P. DeWitt, “Fundamentals of Heat and Mass Transfer”, 4th Edition, 1996
References:

## Slide 9
Combined Convection and Radiation Heat Transfer
Consider a surface with size and at temperature which is transferring heat to an adjacent environment through simultaneous via convection and radiation.
The total heat transfer from the wall is:
where:
= convection heat transfer coefficient ()
= radiation heat transfer coefficient ()
When assessing heat transfer from a building surface to surroundings, it’s often reasonable to treat (i.e. surfaces viewed by the wall have average close to that of the adjacent air). This can be a reasonable approximation for both interior and exterior surfaces. Applying this to the previous equation:
= combined conv. & rad. heat transfer coefficient,
= temperature of the adjacent air (at sufficient distance from wall such that to be “unaffected” by the wall).
= representative temperature of the surroundings that have “line of sight” to the wall for radiant heat exchanger (e.g. hemisphere in view of wall).

## Slide 10
Let’s now denote the total heat transfer from surface to surroundings simply as and denote the size of the surface as (i.e. drop the subscripts). Then:
The planar resistance of this convection and radiation resistance “layer” separating and :
Note: Often the subscript “comb” is dropped from notation, and the combined heat transfer coefficient is simply denoted as .

## Slide 11
For steady heat flow between two temperature nodes separated by a series of resistance layers, the total planar resistance is the sum of the layer planar resistances.
For example, heat flow between two environments separated by a two-layer wall:
Steady 1D Heat Transmission through a Series of Planar Layers
3.
air
(indoors)
air
(outdoors)
material
1
material
2
indoor
combined
HT coeff.
outdoor
combined
HT coeff.

## Slide 12
Example:
Determine the 1-D U-value for a plywood wall (13 mm thick, k ≈ 0.12 W/mK) if , . Then, estimate the steady heat transfer rate when the indoor and outdoor temperatures are = 20C and = -10C, respectively, if = 50 m2.

## Slide 13
Consider a scenario where heat is transmitted between two environment through several independent parallel paths. The total heat transfer is the sum of the flows through the separate paths.
The example below shows three surfaces with different values. The total steady heat transmission is:
Let:
An average U-value, , for the overall surface area, , can be determined.
Parallel Heat Transmission Paths
4.

## Slide 14
A simpler version of the previous diagram:
Example Calculation
During a winter night, a room is maintained at 20C while the outdoor temperature is -10C. Heat is lost from the room through the walls, windows, and roof.
Assembly | Effective Thermal Transmittance, U (W/m2K) | Surface Area (m2)
A) Walls | 0.40 | 16
B) Windows | 2.00 | 6
C) Roof | 0.20 | 16
Determine:
Steady rate of heating needed to maintain the room temperature (W).
Assess the relative contribution of each heat loss path to the total heat loss.

## Slide 15
Consider a room to be kept heated to a steady temperature . The room loses heat due to thermal transmission to the outdoors through two surfaces (e.g, wall and window). It also experiences heat loss due air exchange with the outdoors at rate . The air inside the room is sufficiently well mixed such that it can be treated as uniform temperature.
Assess the steady heating rate () needed to maintain the room temperature if there are no other significant energy flows beyond those depicted.
Steady state energy balance for the CV:
= +
Solve for the heating rate:
= +
If then:
Heat Loss through Parallel Transmission and Ventilation
5.
overall heat loss factor, W/K

## Slide 16
(total heat loss)

## Slide 17
Aspects Of Psychrometric Analysis

## Slide 18
Consider a mixture of ideal gases consisting of “dry air” plus water vapor, H2O.
mixture total pressure (absolute)
temperature (drybulb) of mixture
total volume occupied by mixture
mass of “dry air” (kg)
mass of H2O vapor (kg)
Consider a moist airstream flowing past a location where the mixture properties are T, and volumetric flowrate is .
mixture enthalpy per kga
enthalpy of dry air, kJ/kga
enthalpy of H2O vapor, kJ/kgv
humidity ratio, kgv/kga
Nomenclature for Psychrometric Analysis
6.

## Slide 19
The chart allows simple evaluation of moist-air mixture properties.
Each chart applies to a particular total mixture pressure (i.e. barometric pressure).
Psychrometric Chart
7.
sensible heating
heating &
humidifying
cooling &
humidifying
cooling &
dehumidifying
heating &
dehumidifying
latent heating
(humidifying)
latent cooling
(dehumidifying)
sensible cooling
sensible cooling
Process Direction:

## Slide 20
Psychrometric chart downloaded from Wikimedia Commons (Jan 27, 2017). Author: ArthurOgawa. http://commons.wikimedia.org/wiki/File:PsychrometricChart.SeaLevel.SI.svg
Used under the Creative Commons Attribution-Share Alike 3.0 Unported, 2.5 Generic, 2.0 Generic and 1.0 Generic license.

## Slide 21
Basic Air-Conditioning Processes
8.
Sensible heating/cooling
Cooling with dehumidification
Adiabatic mixing (without condensate production)

## Slide 22
Sensible Heating/Cooling
A sensible heating/cooling process means that there is no change in the amount of moisture carried by the air stream, .
Sensible Heating SS-SF,
E-bal:
Sensible Cooling SS-SF,
E-bal:
1
2
sensible heating
1
2
sensible cooling

## Slide 23
A cooling process will typically result in some of the vapor being carried by the air stream to condense to liquid. Thus, the leaving air stream has lower and than the entering stream.
Energy Balance (CV is the cooled air stream):
SS-SF,
Rate of condensate production
Typically:
1
2
heat removed
by cooling coil
rate of condensate
production (kgw/s)
enthalpy of condensate
(kJ/kgw)
cooling coil
air in
air out
condensate pan
condensate
out
Cooling with Dehumidification

## Slide 24
Adiabatic mixing occurs when two air streams are mixed and there is negligible heat transfer between the CV and its surroundings. Consider only conditions where the mixing causes no condensate production (i.e. all moisture contained by the entering air streams is carried out by the leaving air stream).
Mass balance (dry air):
Mass balance (H2O):
Energy balance (H2O):
1
SS-SF,
2
3
(adiabatic)
Note: On the psychrometric chart, State 3 will lie along a line connecting States 1 and 2.
Adiabatic Mixing (without Condensate Production)